{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["Steam Line 0.5\" SW Stop Valve","Steam Line 1.5\" SW Stop Valve"],"not_rendered":{"images":2,"defined_names":2},"read":"whole","date_system":"1900"}

{"sheet":"Steam Line 0.5\" SW Stop Valve","index":0,"n_rows":67,"n_cols":25,"rows_kept":67,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,26],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,26],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,26],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,26],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,26],[12,1,12,26],[13,4,13,11],[13,12,13,14],[13,15,13,25],[14,3,23,3],[14,4,14,11],[14,12,14,14],[14,15,14,25],[15,4,15,11],[15,12,15,14],[15,15,15,25],[16,4,16,11],[16,12,16,14],[16,15,16,25],[17,4,17,11],[17,12,17,14],[17,15,17,25],[18,4,18,11],[18,12,18,14],[18,15,18,25],[19,4,19,11],[19,12,19,14],[19,15,19,25],[20,4,20,11],[20,12,20,14],[20,15,20,25],[21,4,21,11],[21,12,21,14],[21,15,21,25],[22,4,22,11],[22,12,22,14],[22,15,22,25],[23,4,23,11],[23,12,23,14],[23,15,23,25],[24,3,35,3],[24,4,24,11],[24,12,24,14],[24,15,24,18],[24,19,24,20],[24,21,24,22],[24,24,24,25],[25,4,25,11],[25,12,25,14],[25,15,25,18],[25,19,25,20],[25,21,25,22],[25,24,25,25],[26,4,26,11],[26,12,26,14],[26,15,26,25],[27,4,27,11],[27,12,27,14],[27,15,27,25],[28,4,28,11],[28,12,28,14],[28,15,28,25],[29,4,29,11],[29,12,29,14],[29,15,29,25],[30,4,30,11],[30,12,30,14],[30,15,30,25],[31,4,31,11],[31,12,31,14],[31,15,31,25],[32,4,32,11],[32,12,32,14],[32,15,32,25],[33,4,33,11],[33,12,33,14],[33,15,33,25],[34,4,34,11],[34,12,34,14],[34,15,34,25],[35,4,35,11],[35,12,35,14],[35,15,35,25],[36,3,48,3],[36,4,36,11],[36,12,36,14],[36,15,36,25],[37,4,37,11],[37,12,37,14],[37,15,37,25],[38,4,38,11],[38,12,38,14],[38,15,38,25],[39,4,39,11],[39,12,39,14],[39,15,39,25],[40,4,40,11],[40,12,40,14],[40,15,40,25],[41,4,41,11],[41,12,41,14],[41,15,41,25],[42,4,42,11],[42,12,42,14],[42,15,42,25],[43,4,43,11],[43,12,43,14],[43,15,43,25],[44,4,44,11],[44,12,44,14],[44,15,44,25],[45,4,45,11],[45,12,45,14],[45,15,45,25],[46,4,46,11],[46,12,46,14],[46,15,46,25],[47,4,47,11],[47,12,47,14],[47,15,47,25],[48,4,48,11],[48,12,48,14],[48,15,48,25],[49,3,56,3],[49,4,49,11],[49,12,49,14],[49,15,49,25],[50,4,50,11],[50,12,50,14],[50,15,50,25],[51,4,51,11],[51,12,51,14],[51,15,51,25],[52,4,52,11],[52,12,52,14],[52,15,52,25],[53,4,53,11],[53,12,53,14],[53,15,53,25],[54,4,54,11],[54,12,54,14],[54,15,54,25],[55,4,55,11],[55,12,55,14],[55,15,55,25],[56,4,56,11],[56,12,56,14],[56,15,56,25],[57,3,66,3],[57,4,57,11],[57,12,57,14],[57,15,57,25],[58,4,58,11],[58,12,58,14],[58,15,58,25],[59,4,59,11],[59,12,59,14],[59,15,59,25],[60,4,60,11],[60,12,60,14],[60,15,60,25],[61,4,61,11],[61,12,61,14],[61,15,61,25],[62,4,62,11],[62,12,62,14],[62,15,62,25],[63,4,63,11],[63,12,63,14],[63,15,63,25],[64,4,64,11],[64,12,64,14],[64,15,64,25],[65,4,65,11],[65,12,65,14],[65,15,65,25],[66,4,66,11],[66,12,66,14],[66,15,66,25],[67,1,67,6],[67,7,67,9],[68,1,68,6],[68,7,68,9],[69,1,69,6],[69,7,69,8]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-002"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
[null,"Item:",null,null,"Ball Valves Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",null,"2021-09-11",null,null,"MJ",{"$nulls":3},"JvdW",{"$nulls":3},"CP",{"$nulls":3},"Issued for Internal Review"]
[]
[null,"Data Sheet for 1/2\" Socket Weld Stop Valves"]
[null,"No","Rev","Section","Description",{"$nulls":10},"Data"]
[null,1,null,"GENERAL DATA","VALVE SIZE RANGE",{"$nulls":5},"Inch (mm)",{"$nulls":4},"1/2\""]
[null,2,null,null,"VALVE ASME CLASS",{"$nulls":10},"300 - SCH40"]
[null,3,null,null,"VALVE TYPE",{"$nulls":10},"Stop Valve"]
[null,4,null,null,"VALVE END CONFIGURATION",{"$nulls":10},"Socket Weld"]
[null,5,null,null,"VALVE SERVICE",{"$nulls":10},"Steam"]
[null,6,null,null,"VALVE TAG NUMBER"]
[null,7,null,null,"QUANTITY",{"$nulls":10},8]
[null,8,null,null,"VALVE BORE (FULL / REDUCED)",{"$nulls":10},"Full Bore"]
[null,9,null,null,"VALVE STANDARD ",{"$nulls":10},"ASME B16.34 / API 608 or similar"]
[null,10,null,null,"PIGGABLE",{"$nulls":10},"No"]
[null,11,null,"DESIGN DATA","DESIGN PRESSURE (kPa)",{"$nulls":5},"barg",null,"MAXIMUM:",null,null,2500,{"$nulls":5},"MINIMUM:",null,null,"Full Vacuum"]
[null,12,null,null,"TEMPERATURE - DESIGN (°C)",{"$nulls":5},"°C",null,"MAXIMUM:",null,null,220,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,13,null,null,"VALVE ACTUATOR",{"$nulls":10},"N/A"]
[null,14,null,null,"VALVE OPERATION - MANUAL",{"$nulls":10},"Hand wheel"]
[null,15,null,null,"VENT CONNECTION",{"$nulls":10},"N/A"]
[null,16,null,null,"DRAIN CONNECTION",{"$nulls":10},"N/A"]
[null,17,null,null,"PRESSURE RELIEF CONNECTION",{"$nulls":10},"N/A"]
[null,18,null,null,"SEALANT INJECTION CONNECTION",{"$nulls":10},"Manufacturer's Standard"]
[null,19,null,null,"SUPPORT LEGS / FEET",{"$nulls":10},"N/A"]
[null,20,null,null,"LIFTING EYES",{"$nulls":10},"N/A"]
[null,21,null,null,"LOCKING FACILITY",{"$nulls":10},"Yes"]
[null,22,null,null,"SURFACE TREATMENT ",{"$nulls":10},"50 microns Zinc Phosphate Primer + Paint Specification for Above Ground. "]
[null,23,null,"MATERIALS","BODY",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 105"]
[null,24,null,null,"COVER / BONNET",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 105"]
[null,25,null,null,"GLAND FLANGE",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 106"]
[null,26,null,null,"BALL",{"$nulls":10},"Supplier to Advise"]
[null,27,null,null,"DISC",{"$nulls":10},"Stainless Steel ASTM A276"]
[null,28,null,null,"TRIM",{"$nulls":10},"Supplier to Advise"]
[null,29,null,null,"SEALS",{"$nulls":10},"Supplier to Advise"]
[null,30,null,null,"GASKETS",{"$nulls":10},"Manufacturer's Standard - Non Asbestos"]
[null,31,null,null,"STEM",{"$nulls":10},"Supplier to Advise"]
[null,32,null,null,"TRUNNION",{"$nulls":10},"N/A"]
[null,33,null,null,"SEAT / RINGS",{"$nulls":10},"Supplier to Advise"]
[null,34,null,null,"STEM SEAL",{"$nulls":10},"Viton / 316 / Graphite"]
[null,35,null,null,"BOLTING",{"$nulls":10},"ASTM A193 B7, ASTM A194 2H"]
[null,36,null,"CODES AND STANDARDS","DESIGN",{"$nulls":10},"API 6D"]
[null,37,null,null,"DIMENSIONS",{"$nulls":10},"ASME B16.10"]
[null,38,null,null,"THREADED DIMENSIONS",{"$nulls":10},"N/A"]
[null,39,null,null,"FLANGE DIMENSIONS",{"$nulls":10},"N/A"]
[null,40,null,null,"WELD END DIMENSIONS",{"$nulls":10},"ASME B16.11 "]
[null,41,null,null,"CERTIFICATION ",{"$nulls":10},"EN 10204 3.1"]
[null,42,null,null,"FIRE TEST - FIRE SAFE DESIGN",{"$nulls":10},"API 6FA / API 607 / BS 6755 Part 2"]
[null,43,null,null,"HYDROSTATIC TEST",{"$nulls":10},"API 6D - No compressive end loads to be applied"]
[null,44,null,"TESTING REQUIREMENTS","HYDROSTATIC SHELL TEST PRESSURE",{"$nulls":10},"API 598"]
[null,45,null,null,"HYDROSTATIC SEAT TEST PRESSURE",{"$nulls":10},"API 598"]
[null,46,null,null,"HIGH PRESSURE TEST",{"$nulls":10},"API 598"]
[null,47,null,null,"ISO 5208 LEAKAGE RATE FOR SOFT SEAT",{"$nulls":10},"Rate A"]
[null,48,null,null,"ISO 5208 LEAKAGE RATE FOR METAL SEAT",{"$nulls":10},"Rate D"]
[null,49,null,null,"RADIOGRAPHIC TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX I"]
[null,50,null,null,"ULTRASONIC TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX IV"]
[null,51,null,null,"PENETRANT TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX III"]
[null,52,null,null,"MAGNETIC PARTICLE TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX II"]
[null,53,null,null,"MATERIAL CERTIFICATION - EN 10204 3.1.B",{"$nulls":10},"Required"]

{"sheet":"Steam Line 1.5\" SW Stop Valve","index":1,"n_rows":67,"n_cols":25,"rows_kept":67,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,26],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,26],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,26],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,26],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,26],[12,1,12,26],[13,4,13,11],[13,12,13,14],[13,15,13,25],[14,3,23,3],[14,4,14,11],[14,12,14,14],[14,15,14,25],[15,4,15,11],[15,12,15,14],[15,15,15,25],[16,4,16,11],[16,12,16,14],[16,15,16,25],[17,4,17,11],[17,12,17,14],[17,15,17,25],[18,4,18,11],[18,12,18,14],[18,15,18,25],[19,4,19,11],[19,12,19,14],[19,15,19,25],[20,4,20,11],[20,12,20,14],[20,15,20,25],[21,4,21,11],[21,12,21,14],[21,15,21,25],[22,4,22,11],[22,12,22,14],[22,15,22,25],[23,4,23,11],[23,12,23,14],[23,15,23,25],[24,3,35,3],[24,4,24,11],[24,12,24,14],[24,15,24,18],[24,19,24,20],[24,21,24,22],[24,24,24,25],[25,4,25,11],[25,12,25,14],[25,15,25,18],[25,19,25,20],[25,21,25,22],[25,24,25,25],[26,4,26,11],[26,12,26,14],[26,15,26,25],[27,4,27,11],[27,12,27,14],[27,15,27,25],[28,4,28,11],[28,12,28,14],[28,15,28,25],[29,4,29,11],[29,12,29,14],[29,15,29,25],[30,4,30,11],[30,12,30,14],[30,15,30,25],[31,4,31,11],[31,12,31,14],[31,15,31,25],[32,4,32,11],[32,12,32,14],[32,15,32,25],[33,4,33,11],[33,12,33,14],[33,15,33,25],[34,4,34,11],[34,12,34,14],[34,15,34,25],[35,4,35,11],[35,12,35,14],[35,15,35,25],[36,3,48,3],[36,4,36,11],[36,12,36,14],[36,15,36,25],[37,4,37,11],[37,12,37,14],[37,15,37,25],[38,4,38,11],[38,12,38,14],[38,15,38,25],[39,4,39,11],[39,12,39,14],[39,15,39,25],[40,4,40,11],[40,12,40,14],[40,15,40,25],[41,4,41,11],[41,12,41,14],[41,15,41,25],[42,4,42,11],[42,12,42,14],[42,15,42,25],[43,4,43,11],[43,12,43,14],[43,15,43,25],[44,4,44,11],[44,12,44,14],[44,15,44,25],[45,4,45,11],[45,12,45,14],[45,15,45,25],[46,4,46,11],[46,12,46,14],[46,15,46,25],[47,4,47,11],[47,12,47,14],[47,15,47,25],[48,4,48,11],[48,12,48,14],[48,15,48,25],[49,3,56,3],[49,4,49,11],[49,12,49,14],[49,15,49,25],[50,4,50,11],[50,12,50,14],[50,15,50,25],[51,4,51,11],[51,12,51,14],[51,15,51,25],[52,4,52,11],[52,12,52,14],[52,15,52,25],[53,4,53,11],[53,12,53,14],[53,15,53,25],[54,4,54,11],[54,12,54,14],[54,15,54,25],[55,4,55,11],[55,12,55,14],[55,15,55,25],[56,4,56,11],[56,12,56,14],[56,15,56,25],[57,3,66,3],[57,4,57,11],[57,12,57,14],[57,15,57,25],[58,4,58,11],[58,12,58,14],[58,15,58,25],[59,4,59,11],[59,12,59,14],[59,15,59,25],[60,4,60,11],[60,12,60,14],[60,15,60,25],[61,4,61,11],[61,12,61,14],[61,15,61,25],[62,4,62,11],[62,12,62,14],[62,15,62,25],[63,4,63,11],[63,12,63,14],[63,15,63,25],[64,4,64,11],[64,12,64,14],[64,15,64,25],[65,4,65,11],[65,12,65,14],[65,15,65,25],[66,4,66,11],[66,12,66,14],[66,15,66,25],[67,1,67,6],[67,7,67,9],[68,1,68,6],[68,7,68,9],[69,1,69,6],[69,7,69,8]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-002"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
[null,"Item:",null,null,"Ball Valves Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",null,"2021-09-11",null,null,"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[null,"Data Sheet for 1 1/2\" Socket Weld Stop Valves"]
[null,"No","Rev","Section","Description",{"$nulls":10},"Data"]
[null,1,null,"GENERAL DATA","VALVE SIZE RANGE",{"$nulls":5},"Inch (mm)",{"$nulls":4},"1 1/2\""]
[null,2,null,null,"VALVE ASME CLASS",{"$nulls":10},"300 - SCH40"]
[null,3,null,null,"VALVE TYPE",{"$nulls":10},"Stop Valve"]
[null,4,null,null,"VALVE END CONFIGURATION",{"$nulls":10},"Socket Weld"]
[null,5,null,null,"VALVE SERVICE",{"$nulls":10},"Steam"]
[null,6,null,null,"VALVE TAG NUMBER",{"$nulls":10},"A3S or A3SS - Spirax Sarco"]
[null,7,null,null,"QUANTITY",{"$nulls":10},1]
[null,8,null,null,"VALVE BORE (FULL / REDUCED)",{"$nulls":10},"Full Bore"]
[null,9,null,null,"VALVE STANDARD ",{"$nulls":10},"ASME B16.34 / API 608 or similar"]
[null,10,null,null,"PIGGABLE",{"$nulls":10},"No"]
[null,11,null,"DESIGN DATA","DESIGN PRESSURE (kPa)",{"$nulls":5},"barg",null,"MAXIMUM:",null,null,2500,{"$nulls":5},"MINIMUM:",null,null,"Full Vacuum"]
[null,12,null,null,"TEMPERATURE - DESIGN (°C)",{"$nulls":5},"°C",null,"MAXIMUM:",null,null,220,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,13,null,null,"VALVE ACTUATOR",{"$nulls":10},"N/A"]
[null,14,null,null,"VALVE OPERATION - MANUAL",{"$nulls":10},"Hand wheel"]
[null,15,null,null,"VENT CONNECTION",{"$nulls":10},"N/A"]
[null,16,null,null,"DRAIN CONNECTION",{"$nulls":10},"N/A"]
[null,17,null,null,"PRESSURE RELIEF CONNECTION",{"$nulls":10},"N/A"]
[null,18,null,null,"SEALANT INJECTION CONNECTION",{"$nulls":10},"Manufacturer's Standard"]
[null,19,null,null,"SUPPORT LEGS / FEET",{"$nulls":10},"N/A"]
[null,20,null,null,"LIFTING EYES",{"$nulls":10},"N/A"]
[null,21,null,null,"LOCKING FACILITY",{"$nulls":10},"Yes"]
[null,22,null,null,"SURFACE TREATMENT ",{"$nulls":10},"50 microns Zinc Phosphate Primer + Paint Specification for Above Ground. "]
[null,23,null,"MATERIALS","BODY",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 105"]
[null,24,null,null,"COVER / BONNET",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 105"]
[null,25,null,null,"GLAND FLANGE",{"$nulls":10},"Carbon Steel (API 6D Approved) ASTM A 106"]
[null,26,null,null,"BALL",{"$nulls":10},"Supplier to Advise"]
[null,27,null,null,"DISC",{"$nulls":10},"Stainless Steel ASTM A276"]
[null,28,null,null,"TRIM",{"$nulls":10},"Supplier to Advise"]
[null,29,null,null,"SEALS",{"$nulls":10},"Supplier to Advise"]
[null,30,null,null,"GASKETS",{"$nulls":10},"Manufacturer's Standard - Non Asbestos"]
[null,31,null,null,"STEM",{"$nulls":10},"Supplier to Advise"]
[null,32,null,null,"TRUNNION",{"$nulls":10},"N/A"]
[null,33,null,null,"SEAT / RINGS",{"$nulls":10},"Supplier to Advise"]
[null,34,null,null,"STEM SEAL",{"$nulls":10},"Viton / 316 / Graphite"]
[null,35,null,null,"BOLTING",{"$nulls":10},"ASTM A193 B7, ASTM A194 2H"]
[null,36,null,"CODES AND STANDARDS","DESIGN",{"$nulls":10},"API 6D"]
[null,37,null,null,"DIMENSIONS",{"$nulls":10},"ASME B16.10"]
[null,38,null,null,"THREADED DIMENSIONS",{"$nulls":10},"N/A"]
[null,39,null,null,"FLANGE DIMENSIONS",{"$nulls":10},"N/A"]
[null,40,null,null,"WELD END DIMENSIONS",{"$nulls":10},"ASME B16.11 "]
[null,41,null,null,"CERTIFICATION ",{"$nulls":10},"EN 10204 3.1"]
[null,42,null,null,"FIRE TEST - FIRE SAFE DESIGN",{"$nulls":10},"API 6FA / API 607 / BS 6755 Part 2"]
[null,43,null,null,"HYDROSTATIC TEST",{"$nulls":10},"API 6D - No compressive end loads to be applied"]
[null,44,null,"TESTING REQUIREMENTS","HYDROSTATIC SHELL TEST PRESSURE",{"$nulls":10},"API 598"]
[null,45,null,null,"HYDROSTATIC SEAT TEST PRESSURE",{"$nulls":10},"API 598"]
[null,46,null,null,"HIGH PRESSURE TEST",{"$nulls":10},"API 598"]
[null,47,null,null,"ISO 5208 LEAKAGE RATE FOR SOFT SEAT",{"$nulls":10},"Rate A"]
[null,48,null,null,"ISO 5208 LEAKAGE RATE FOR METAL SEAT",{"$nulls":10},"Rate D"]
[null,49,null,null,"RADIOGRAPHIC TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX I"]
[null,50,null,null,"ULTRASONIC TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX IV"]
[null,51,null,null,"PENETRANT TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX III"]
[null,52,null,null,"MAGNETIC PARTICLE TESTS",{"$nulls":10},"ASME B16.34 \nAPPENDIX II"]
[null,53,null,null,"MATERIAL CERTIFICATION - EN 10204 3.1.B",{"$nulls":10},"Required"]