{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["BOQ","Data Plate Particulars"],"read":"whole","date_system":"1900"}

{"sheet":"BOQ","index":0,"n_rows":23,"n_cols":16,"rows_kept":23,"merged":[[0,0,0,3],[1,3,1,12],[20,2,20,14],[21,2,21,14],[22,2,22,14]]}
["ANNEXURE B : BILL OF QUANTITIES"]
[{"$nulls":3},"DATA PLATE PARTICULARS MINIMUM REQUIREMENT AS PER SA PRESSURE EQUIPMENT REGULATION"]
["#","Location","Vessel Description","Name of  manufacturer","Country of origin","Year of manufacturer","Manufacturer serial number","Ref number, date and edition of H&S standard","Design pressur in units of pascal","Design minimum and maximum  temperature","Capacity in cubic metres","Unique mark of an AIA","Hazard category(SANS 347)","Quantity","Rate for certification inclusive of AIA","Total"]
[1,"Bld 18","Fermenter","B Braun Biotech International","Not indicated",1995,"050-5","Not indicated","300 kPa","150^oc","Shell 0.015m^3 and Jacket 0.020m^3","Not indicated","Not indicated",1]
[2,"Bld 18","Fermenter","B Braun Biotech International","Not indicated",1995,"205-1","Not indicated","300 kPa","150^oc","Shell 0.015m^3 and Jacket 0.020m^3","Not indicated","Not indicated",1]
[3,"Bld 18 room C34","Autoclave","Systec","Not indicated",2008,2356,"Not indicated","400kPa","150^oc","0.075m^3","Not indicated","Not indicated",1]
[4,"Bld 18","Fermenter","Sartorius Stedim Biotech","India",2015,4957,"ASME VIII Div 1 2013","Shell 300 kPa and Jacket 400 kPa","Minus 10^0c  to 150^0c","Shell 0.042m^3 and Jacket 0.036m^3","Not indicated","Not indicated",1]
[5,"Bld 18","Autoclave","ALP co. LTD","Japan",2014,805809,"Not indicated","0.27MPa","Not indicated","0.097m^3","Not indicated","Not indicated",1]
[6,"Bld 18","Fermenter","Sartorius Stedim Biotech","India",2015,4959,"ASME VIII Div 1 2013","Shell 300 kPa and Jacket 400 kPa","Minus 10^0c  to 150^0c","Shell 0.042m^3 and Jacket 0.036m^3","Not indicated","Not indicated",1]
[7,"Bld 18","Fermenter","B Braun + Diesel Biotech Gmb","Not indicated",1992,"217/300DS","Not indicated","minus1bar to 3 bar","150^OC","3m^3","Not indicated","Not indicated",1]
[8,"Bld 18","Reactor vessel","Not indicated","Not indicated",19999,"660hc10-1194","ASME (U stamp)","1900 Psi","Minus 20F  to 662F","Not indicated","ASME (U stamp)","Not indicated",1]
[9,"Bld 18","Fermenter","Turttnauer","Israel",2014,1302216,"ASME (U stamp)","280 kPa","15^oc to 100^oc","0.4m^3","Not indicated","Not indicated",1]
[10,"Bld 20 room S137","Autoclave","Not indicated","Not indicated","Not indicated","S0407021","Not indicated","245kPa","150^oc","0.075m^3","Not indicated","Not indicated",1]
[11,"Bld 20 room S241","Autoclave","Not indicated","Not indicated",2007,"S0708124","Not indicated","245kPa","150^oc","0.075m^3","Not indicated","Not indicated",1]
[12,"Bld 20 room 137","Autoclave","Not indicated","Not indicated",2013,"S1306011","Not indicated","245kPa","150^oc",0.095,"Not indicated","Not indicated",1]
[13,"Bld 14","Autoclave","Not indicated","Not indicated",1995,"S014080006","Not indicated","250 kPa","132^oc","0.099 m^3","Not indicated","Not indicated",1]
[14,"Bld 18D","Pressure pot","Not indicated","Not indicated",1981,"AB2534","Not indicated","350kPa","Not indicated","0.008m^3","Not indicated","Not indicated",1]
[15,"Bld 2","Compressor Air receiver","Kaeser","Not indicated",2008,372151,"Not indicated","1150 kPa","minus 10 to 120^oc","0.215 m^3","CE 0036","Not indicated",1]
[16,"Bld 2","Autoclave","ATS","Not indicated","Not indicated","09-5062-1-10","Not indicated","250kPa","90 to 110^oc","1 M^3","Not indicated","Not indicated",1]
[17,"Bld 2","Compressor Air receiver","CSL SRL","Italy",2010,17382,"Not indicated","1100 kPa","minus 10 to 100^oc","0.5 m^3","CE 0060","Not indicated",1]
[null,null,"Sub-Total"]
[null,null,"Add 15% VAT"]
[null,null,"Total"]

{"sheet":"Data Plate Particulars","index":1,"n_rows":20,"n_cols":13,"rows_kept":20,"merged":[[1,0,2,0],[1,1,2,1],[1,2,1,11],[1,12,2,12]]}
[]
["Location","Vessel Description","DATA PLATE PARTICULARS MINIMUM REQUIREMENT AS PER SA PRESSURE EQUIPMENT REGULATION",{"$nulls":9},"Comments/action to ensure compliance"]
[null,null,"Name of  manufacturer","Country of origin","Year of manufacturer","Manufacturer serial number","Ref number, date and edition of H&S standard","Design pressur in units of pascal","Design minimum and maximum  temperature","Capacity in cubic metres","Unique mark of an AIA","Hazard category(SANS 347)"]
["Bld 18","Fermenter","B Braun Biotech International","Not indicated",1995,"050-5","Not indicated","300 kPa","150^oc","Shell 0.015m^3 and Jacket 0.020m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Fermenter","B Braun Biotech International","Not indicated",1995,"205-1","Not indicated","300 kPa","150^oc","Shell 0.015m^3 and Jacket 0.020m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18 room C34","Autoclave","Systec","Not indicated",2008,2356,"Not indicated","400kPa","150^oc","0.075m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Fermenter","Sartorius Stedim Biotech","India",2015,4957,"ASME VIII Div 1 2013","Shell 300 kPa and Jacket 400 kPa","Minus 10^0c  to 150^0c","Shell 0.042m^3 and Jacket 0.036m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Autoclave","ALP co. LTD","Japan",2014,805809,"Not indicated","0.27MPa","Not indicated","0.097m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Fermenter","Sartorius Stedim Biotech","India",2015,4959,"ASME VIII Div 1 2013","Shell 300 kPa and Jacket 400 kPa","Minus 10^0c  to 150^0c","Shell 0.042m^3 and Jacket 0.036m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Fermenter","B Braun + Diesel Biotech Gmb","Not indicated",1992,"217/300DS","Not indicated","minus1bar to 3 bar","150^OC","3m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Reactor vessel","Not indicated","Not indicated",19999,"660hc10-1194","ASME (U stamp)","1900 Psi","Minus 20F  to 662F","Not indicated","ASME (U stamp)","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18","Fermenter","Turttnauer","Israel",2014,1302216,"ASME (U stamp)","280 kPa","15^oc to 100^oc","0.4m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 20 room S137","Autoclave","Not indicated","Not indicated","Not indicated","S0407021","Not indicated","245kPa","150^oc","0.075m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 20 room S241","Autoclave","Not indicated","Not indicated",2007,"S0708124","Not indicated","245kPa","150^oc","0.075m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 20 room 137","Autoclave","Not indicated","Not indicated",2013,"S1306011","Not indicated","245kPa","150^oc",0.095,"Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 14","Autoclave","Not indicated","Not indicated",1995,"S014080006","Not indicated","250 kPa","132^oc","0.099 m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 18D","Pressure pot","Not indicated","Not indicated",1981,"AB2534","Not indicated","350kPa","Not indicated","0.008m^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 2","Compressor Air receiver","Kaeser","Not indicated",2008,372151,"Not indicated","1150 kPa","minus 10 to 120^oc","0.215 m^3","CE 0036","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 2","Autoclave","ATS","Not indicated","Not indicated","09-5062-1-10","Not indicated","250kPa","90 to 110^oc","1 M^3","Not indicated","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]
["Bld 2","Compressor Air receiver","CSL SRL","Italy",2010,17382,"Not indicated","1100 kPa","minus 10 to 100^oc","0.5 m^3","CE 0060","Not indicated","Obtain certificate of manufacturer in order to make a new data plate that comply to VUP under supervision of an AIA- Manufacturing” or Obtain new Data plate from supplier/manufacturer or Recertification is required (worst case scenario)"]