{"text_format":"3","workbook":"xlsx","n_sheets":5,"sheets":["Nitrogen Line_","Compressed Air Line","Municipal Water Line","Hot Water Line","Steam Line"],"not_rendered":{"images":2,"defined_names":5},"read":"whole","date_system":"1900"}

{"sheet":"Nitrogen Line_","index":0,"n_rows":43,"n_cols":26,"rows_kept":43,"merged":[[0,0,0,2],[0,3,0,11],[0,12,4,16],[0,17,4,23],[1,0,1,2],[1,3,1,11],[2,0,2,2],[2,3,2,11],[3,0,3,2],[3,3,3,11],[4,0,4,2],[4,3,4,11],[5,0,5,23],[6,0,6,1],[6,2,6,4],[6,5,6,8],[6,9,6,12],[6,13,6,16],[6,17,6,23],[7,0,7,1],[7,2,7,4],[7,5,7,8],[7,9,7,12],[7,13,7,16],[7,17,7,23],[8,0,8,1],[8,2,8,4],[8,5,8,8],[8,9,8,12],[8,13,8,16],[8,17,8,23],[9,0,9,1],[9,2,9,4],[9,5,9,8],[9,9,9,12],[9,13,9,16],[9,17,9,23],[10,0,10,1],[10,2,10,4],[10,5,10,8],[10,9,10,12],[10,13,10,16],[10,17,10,23],[11,0,11,1],[11,2,11,4],[11,5,11,8],[11,9,11,12],[11,13,11,16],[11,17,11,23],[12,0,12,23],[13,3,13,10],[13,11,13,23],[14,2,29,2],[14,3,14,10],[14,11,14,13],[14,14,14,23],[15,3,15,10],[15,11,15,13],[15,14,15,23],[16,3,16,10],[16,11,16,13],[16,14,16,23],[17,3,17,7],[17,8,17,10],[17,11,17,13],[17,14,17,23],[18,3,18,10],[18,11,18,13],[18,14,18,17],[18,18,18,19],[18,20,18,21],[18,29,18,32],[19,3,19,10],[19,11,19,13],[19,14,19,23],[20,3,20,10],[20,11,20,13],[20,14,20,23],[21,3,21,10],[21,11,21,13],[21,14,21,23],[22,3,22,10],[22,11,22,13],[22,14,22,23],[23,3,23,10],[23,11,23,13],[23,14,23,23],[24,3,24,23],[24,29,24,32],[25,4,25,23],[26,4,26,23],[26,29,26,32],[27,4,27,23],[27,29,27,32],[28,4,28,23],[28,29,28,32],[29,4,29,23],[30,2,42,2],[30,3,30,5],[30,6,30,10],[30,11,30,13],[30,14,30,23],[30,25,30,28],[31,3,31,5],[31,6,31,10],[31,11,31,13],[31,14,31,23],[31,25,31,28],[32,3,32,28],[33,6,33,10],[33,11,33,13],[33,14,33,23],[33,25,34,28],[34,3,34,5],[34,6,34,10],[34,11,34,13],[34,14,34,23],[35,3,35,5],[35,6,35,10],[35,11,35,13],[35,14,35,23],[35,25,35,28],[36,3,36,5],[36,6,36,10],[36,11,36,13],[36,14,36,23],[36,25,36,28],[37,3,37,5],[37,6,37,10],[37,11,37,13],[37,14,37,23],[37,25,37,28],[38,3,38,28],[39,3,39,5],[39,6,39,10],[39,11,39,13],[39,14,39,23],[39,25,39,28],[40,3,40,28],[41,3,41,5],[41,6,41,10],[41,11,41,13],[41,14,41,23],[41,25,41,28],[42,3,42,5],[42,6,42,10],[42,11,42,13],[42,14,42,23],[42,25,42,28]]}
["Project",null,null,"BIDF Expansion"]
["Document No:",null,null,"21050-CSI-ME-DAS-001"]
["Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
["Item:",null,null,"Nitrogen Line Connections Data Sheet"]
["Page:",null,null,"1 of 1"]
["Revision Tracking"]
["Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
["A",{"$nulls":4},"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[]
[]
[]
["Data Sheet for Nitrogen Line Connections and Tubing"]
["No","Rev","Section","Data",{"$nulls":7},"Description"]
[1,null,"DESIGN DATA","TRANSPORTED FLUID",{"$nulls":10},"Nitrogen"]
[2,null,null,"LOCATION",{"$nulls":10},"Above Ground"]
[3,null,null,"DESIGN LIFE",{"$nulls":10},"25 years"]
[4,null,null,"PIPELINE DESIGN PRESSURE",{"$nulls":4},"Barg",{"$nulls":5},25]
[5,null,null,"PIPELINE TEMPERATURE - DESIGN ",{"$nulls":5},"°C",null,"MAXIMUM",null,null,65,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[6,null,null,"SERVICE TYPE (Sour/ Non-sour)",{"$nulls":5},"barg",{"$nulls":4},"Non-sour"]
[7,null,null,"TUBING MATERIAL",{"$nulls":10},"Medical Grade Copper SANS 1453:2011 (Imperial)"]
[8,null,null,"TUBING FITTING MATERIAL",{"$nulls":10},"VTC"]
[9,null,null,"TUBING FITTING THREAD",{"$nulls":10},"NPT and BSP"]
[10,null,null,"TUBING FITTING TYPE",{"$nulls":10},"Compression fitting (Ferrule type) (VTC)"]
[11,null,null,"Notes"]
[12,null,null,1,"VTC - VENDOR TO CONFIRM "]
[13,null,null,2,"Supplier to confirm tubing for specified Pressures and Temperatures"]
[14]
[15]
[16,{"$nulls":13},"VENDOR TO CONFIRM "]
[17,null,"Material and Quantities","Description",null,null,"End Connection",{"$nulls":4},"Size",null,null,"Quantity",{"$nulls":9},"Connection Material","Notes"]
[18,null,null,"Medical Cu Tube",null,null,"-",{"$nulls":4},"3/8\"",null,null,"30.48mtrs 2 rols of 15,24mtrs (Note 2)"]
[19,null,null,"PID 10 - Main Utilities Connections"]
[20,null,null,"Male connector",null,null,"3/8\" tube X 1/2\" npt male",{"$nulls":4},"3/8\"",null,null,2,{"$nulls":9},"Brass"]
[21,null,null,"Male Plug",null,null,"1/2\"",{"$nulls":4},"1/2\"",null,null,2,{"$nulls":9},"Brass"]
[22,null,null,"Tee Piece",null,null,"3 x Cu Tube Connection",{"$nulls":4},"3/8\"",null,null,7,{"$nulls":9},"Brass"]
[23,null,null,"Elbow",null,null,"2 x Cu Tube Connection",{"$nulls":4},"3/8\"",null,null,6,{"$nulls":9},"Brass"]
[24,null,null,"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"1/2\" NPT x 3/8\" Tube",null,null,6,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves"]
[25,null,null,"PID 2 - Parr Stirred Digester"]
[26,null,null,"Female Connector",null,null,"Threaded End x Cu Tube Connection",{"$nulls":4},"1/4\" NPT x 3/8\" Tube",null,null,"1 (Note 1)",{"$nulls":9},"Brass","To Connect to SS Flexible Hose exsiting 1/4\" male thread on hose on site"]
[27,null,null,"PID 4 - RDH Digester"]
[28,null,null,"Straight Coupler",null,null,"Medical copper Tube x SS316 Tube",{"$nulls":4},"3/8\" Tube x 3/8\" Tube",null,null,"1 (Note 1)",{"$nulls":9},"VTC"]
[29,null,null,"Male Connector",null,null,"SS Threaded End x SS316 Tube",{"$nulls":4},"3/8\" BSPP x 3/8\" Tube",null,null,"1 (Note 1)",{"$nulls":9},"VTC","RDH G3/8\" Socket"]

{"sheet":"Compressed Air Line","index":1,"n_rows":51,"n_cols":27,"rows_kept":51,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,24],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,24],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,24],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,24],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,24],[12,1,12,2],[12,3,12,5],[12,6,12,9],[12,10,12,13],[12,14,12,17],[12,18,12,24],[13,1,13,2],[13,3,13,5],[13,6,13,9],[13,10,13,13],[13,14,13,17],[13,18,13,24],[14,1,14,2],[14,3,14,5],[14,6,14,9],[14,10,14,13],[14,14,14,17],[14,18,14,24],[15,1,15,24],[16,4,16,11],[16,12,16,24],[17,3,32,3],[17,4,17,11],[17,12,17,14],[17,15,17,24],[18,4,18,11],[18,12,18,14],[18,15,18,24],[19,4,19,11],[19,12,19,14],[19,15,19,24],[20,4,20,8],[20,9,20,11],[20,12,20,14],[20,15,20,24],[21,4,21,11],[21,12,21,14],[21,15,21,18],[21,19,21,20],[21,21,21,22],[22,4,22,11],[22,12,22,14],[22,15,22,24],[23,4,23,11],[23,12,23,14],[23,15,23,24],[24,4,24,11],[24,12,24,14],[24,15,24,24],[25,4,25,11],[25,12,25,14],[25,15,25,24],[26,4,26,11],[26,12,26,14],[26,15,26,24],[27,4,27,24],[28,5,28,24],[29,5,29,24],[30,5,30,24],[31,5,31,24],[32,5,32,24],[33,3,50,3],[33,4,33,6],[33,7,33,11],[33,12,33,14],[33,15,33,24],[33,26,33,29],[34,4,34,6],[34,7,34,11],[34,12,34,14],[34,15,34,24],[34,26,34,29],[35,4,35,29],[36,4,36,6],[36,7,36,11],[36,12,36,14],[36,15,36,24],[36,26,37,29],[37,4,37,6],[37,7,37,11],[37,12,37,14],[37,15,37,24],[38,4,38,6],[38,7,38,11],[38,12,38,14],[38,15,38,24],[38,26,38,29],[39,4,39,6],[39,7,39,11],[39,12,39,14],[39,15,39,24],[39,26,39,29],[40,4,40,6],[40,7,40,11],[40,12,40,14],[40,15,40,24],[40,26,40,29],[41,4,41,29],[42,4,42,6],[42,7,42,11],[42,12,42,14],[42,15,42,24],[42,26,42,29],[43,4,43,6],[43,7,43,11],[43,12,43,14],[43,15,43,24],[43,26,43,29],[44,4,44,29],[45,4,45,6],[45,7,45,11],[45,12,45,14],[45,15,45,24],[45,26,45,29],[46,4,46,29],[47,4,47,6],[47,7,47,11],[47,12,47,14],[47,15,47,24],[47,26,47,29],[48,4,48,29],[49,4,49,6],[49,7,49,11],[49,12,49,14],[49,15,49,24],[49,26,49,29],[50,4,50,6],[50,7,50,11],[50,12,50,14],[50,15,50,24],[50,26,50,29]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-001"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
[null,"Item:",null,null,"Compressed Air Line Connections Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",{"$nulls":4},"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[]
[]
[]
[null,"Data Sheet for Compressed Air Line Connections and Tubing"]
[null,"No","Rev","Section","Data",{"$nulls":7},"Description"]
[null,1,null,"DESIGN DATA","TRANSPORTED FLUID",{"$nulls":10},"Compressed Air"]
[null,2,null,null,"LOCATION",{"$nulls":10},"Above Ground"]
[null,3,null,null,"DESIGN LIFE",{"$nulls":10},"25 years"]
[null,4,null,null,"PIPELINE DESIGN PRESSURE",{"$nulls":4},"Barg",{"$nulls":5},25]
[null,5,null,null,"PIPELINE TEMPERATURE - DESIGN ",{"$nulls":5},"°C",null,"MAXIMUM",null,null,65,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,6,null,null,"SERVICE TYPE (Sour/ Non-sour)",{"$nulls":5},"barg",{"$nulls":4},"Non-sour"]
[null,7,null,null,"TUBING MATERIAL",{"$nulls":10},"Medical Grade Copper SANS 1453:2011 (Imperial)"]
[null,8,null,null,"TUBING FITTING MATERIAL",{"$nulls":10},"VTC"]
[null,9,null,null,"TUBING FITTING THREAD",{"$nulls":10},"NPT and BSP"]
[null,10,null,null,"TUBING FITTING TYPE",{"$nulls":10},"Compression fitting (Ferrule type) (VTC)"]
[null,11,null,null,"Notes"]
[null,12,null,null,1,"VTC - VENDOR TO CONFIRM "]
[null,13,null,null,2,"Supplier to confirm tubing for specified Pressures and Temperatures"]
[null,14]
[null,15]
[null,16,{"$nulls":13},"VENDOR TO CONFIRM "]
[null,17,null,"Material and Quantities","Description",null,null,"End Connection",{"$nulls":4},"Size",null,null,"Quantity",{"$nulls":9},"Connection Material","Notes"]
[null,18,null,null,"Medical Cu Tube",null,null,"1/2\" Medical Grade Copper Tubing",{"$nulls":4},"1/2\"",null,null,"7 Of 5.5m lenths (Note 2)"]
[null,19,null,null,"PID 10 - Main Utilities"]
[null,20,null,null,"Male Connector",null,null,"12/\" tube x 1/2\" NPT",{"$nulls":4},"1/2\"",null,null,2,{"$nulls":9},"Brass"]
[null,21,null,null,"Plug",null,null,"1/2\" NPT  Plug",{"$nulls":4},"1/2\"",null,null,2,{"$nulls":9},"Brass"]
[null,22,null,null,"Tee Piece",null,null,"3 x Cu Tube Connection",{"$nulls":4},"1/2\"",null,null,7,{"$nulls":9},"Brass"]
[null,23,null,null,"Elbow",null,null,"2 x Cu Tube Connection",{"$nulls":4},"1/2\"",null,null,10,{"$nulls":9},"Brass"]
[{"$nulls":4},"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"1/2\" NPT x 1/2\" Tube",null,null,10,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves"]
[{"$nulls":4},"PID 9 - LC Refiner and Valley Beater"]
[null,25,null,null,"Female Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"3/8\" NPT x 1/2\" Tube",null,null,2,{"$nulls":9},"Brass","To Connect to Quickfit Air Nipple 3/8\""]
[null,26,null,null,"Reducing Union",null,null,"Threaded End x Flex Hose Nipple",{"$nulls":4},"1/2\" Tube x 3/8\" Tube",null,null,2,{"$nulls":10},"To Connect to polyeurethane 3/8\" Flex Hose - 1 ftting connect from 1/2\" copper to 3/8\" polyu tubing"]
[null,27,null,null,"PID 3 - Flow Through Digester"]
[null,28,null,null,"Female Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"1/4\" NPT x 1/2\" Tube",null,null,1,{"$nulls":9},"Brass","To Connect to Quickfit Air Nipple 6mm"]
[{"$nulls":4},"PID 2 - Parr Stirred Digester"]
[null,29,null,null,"Male Quickfit Nipple",null,null,"Threaded End x Flex Hose Nipple",{"$nulls":4},"1/2\" Tube x 3/8\" Tube",null,null,1,{"$nulls":10},"To Connect to polyeurethane 3/8\" Flex Hose -1 ftting connect from 1/2\" copper to 3/8\" polyu tubing"]
[null,30,null,null,"PID 4 - RDH Digester"]
[null,31,null,null,"Straight Coupler",null,null,"Medical copper Tube x SS316 Tube",{"$nulls":4},"1/2\" Tube x 3/8\" Tube",null,null,"1 (Note 1)",{"$nulls":9},"VTC"]
[null,32,null,null,"Male Connector",null,null,"SS Threaded End x SS316 Tube",{"$nulls":4},"3/8\" BSPP x 3/8\" Tube",null,null,"1 (Note 1)",{"$nulls":9},"VTC","RDH G3/8\" Socket"]

{"sheet":"Municipal Water Line","index":2,"n_rows":67,"n_cols":27,"rows_kept":67,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,24],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,24],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,24],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,24],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,24],[12,1,12,2],[12,3,12,5],[12,6,12,9],[12,10,12,13],[12,14,12,17],[12,18,12,24],[13,1,13,2],[13,3,13,5],[13,6,13,9],[13,10,13,13],[13,14,13,17],[13,18,13,24],[14,1,14,2],[14,3,14,5],[14,6,14,9],[14,10,14,13],[14,14,14,17],[14,18,14,24],[15,1,15,24],[16,4,16,11],[16,12,16,24],[17,3,32,3],[17,4,17,11],[17,12,17,14],[17,15,17,24],[18,4,18,11],[18,12,18,14],[18,15,18,24],[19,4,19,11],[19,12,19,14],[19,15,19,24],[20,4,20,8],[20,9,20,11],[20,12,20,14],[20,15,20,24],[21,4,21,11],[21,12,21,14],[21,15,21,18],[21,19,21,20],[21,21,21,22],[22,4,22,11],[22,12,22,14],[22,15,22,24],[23,4,23,11],[23,12,23,14],[23,15,23,24],[24,4,24,11],[24,12,24,14],[24,15,24,24],[25,4,25,11],[25,12,25,14],[25,15,25,24],[26,4,26,11],[26,12,26,14],[26,15,26,24],[27,4,27,11],[27,12,27,14],[27,15,27,24],[28,4,28,24],[29,5,29,24],[30,5,30,24],[31,5,31,24],[32,5,32,24],[33,4,33,6],[33,7,33,11],[33,12,33,14],[33,15,33,24],[33,26,33,29],[34,4,34,6],[34,7,34,11],[34,12,34,14],[34,15,34,24],[34,26,34,29],[35,4,35,6],[35,7,35,11],[35,12,35,14],[35,15,35,24],[35,26,35,29],[36,4,36,6],[36,7,36,11],[36,12,36,14],[36,15,36,24],[36,26,36,29],[37,4,37,6],[37,7,37,11],[37,12,37,14],[37,15,37,24],[37,26,37,29],[38,4,38,29],[39,4,39,6],[39,7,39,11],[39,12,39,14],[39,15,39,24],[39,26,39,29],[40,4,40,6],[40,7,40,11],[40,12,40,14],[40,15,40,24],[40,26,40,29],[41,4,41,6],[41,7,41,11],[41,12,41,14],[41,15,41,24],[41,26,41,29],[42,4,42,6],[42,7,42,11],[42,12,42,14],[42,15,42,24],[42,26,42,29],[43,4,43,29],[44,4,44,6],[44,7,44,11],[44,12,44,14],[44,15,44,24],[44,26,44,29],[45,4,45,6],[45,7,45,11],[45,12,45,14],[45,15,45,24],[45,26,45,29],[46,4,46,6],[46,7,46,11],[46,12,46,14],[46,15,46,24],[46,26,46,29],[47,4,47,6],[47,7,47,11],[47,12,47,14],[47,15,47,24],[47,26,47,29],[48,4,48,29],[49,4,49,6],[49,7,49,11],[49,12,49,14],[49,15,49,24],[49,26,49,29],[50,4,50,6],[50,7,50,11],[50,12,50,14],[50,15,50,24],[50,26,50,29],[51,4,51,6],[51,7,51,11],[51,12,51,14],[51,15,51,24],[51,26,51,29],[52,4,52,6],[52,7,52,11],[52,12,52,14],[52,15,52,24],[52,26,52,29],[53,4,53,6],[53,7,53,11],[53,12,53,14],[53,15,53,24],[53,26,53,29],[54,4,54,29],[55,4,55,6],[55,7,55,11],[55,12,55,14],[55,15,55,24],[55,26,55,29],[56,4,56,6],[56,7,56,11],[56,12,56,14],[56,15,56,24],[56,26,56,29],[57,4,57,6],[57,7,57,11],[57,12,57,14],[57,15,57,24],[57,26,57,29],[58,4,58,6],[58,7,58,11],[58,12,58,14],[58,15,58,24],[58,26,58,29],[59,4,59,29],[60,4,60,6],[60,7,60,11],[60,12,60,14],[60,15,60,24],[60,26,60,29],[61,4,61,6],[61,7,61,11],[61,12,61,14],[61,15,61,24],[61,26,61,29],[62,4,62,6],[62,7,62,11],[62,12,62,14],[62,15,62,24],[62,26,62,29],[63,4,63,6],[63,7,63,11],[63,12,63,14],[63,15,63,24],[63,26,63,29],[64,4,64,6],[64,7,64,11],[64,12,64,14],[64,15,64,24],[64,26,64,29],[65,4,65,29],[66,4,66,6],[66,7,66,11],[66,12,66,14],[66,15,66,24],[66,26,66,29]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-001"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban",{"$nulls":20},"Page 1 of 2"]
[null,"Item:",null,null,"Municipal Water Line Connections Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",{"$nulls":4},"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[]
[]
[]
[null,"Data Sheet for Municipal Water Line Line Connections and Tubing"]
[null,"No","Rev","Section","Data",{"$nulls":7},"Description"]
[{"$nulls":3},"DESIGN DATA","TRANSPORTED FLUID",{"$nulls":10},"Potable Water - Municipal Water"]
[null,1,null,null,"LOCATION",{"$nulls":10},"Above Ground"]
[null,2,null,null,"DESIGN LIFE",{"$nulls":10},"25 years"]
[null,3,null,null,"PIPELINE DESIGN PRESSURE",{"$nulls":4},"Barg",{"$nulls":5},15]
[null,4,null,null,"PIPELINE TEMPERATURE - DESIGN ",{"$nulls":5},"°C",null,"MAXIMUM",null,null,40,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,5,null,null,"SERVICE TYPE (Sour/ Non-sour)",{"$nulls":5},"barg",{"$nulls":4},"Non-sour"]
[null,6,null,null,"TUBING MATERIAL",{"$nulls":10},"SANS 460/2 (Metric and Imperial)"]
[null,7,{"$nulls":13},"ASME 31.3 Stainless Steel 316L Piping"]
[null,8,null,null,"TUBING FITTING MATERIAL",{"$nulls":10},"VTC"]
[null,9,null,null,"TUBING FITTING THREAD",{"$nulls":10},"NPT and BSP"]
[null,10,null,null,"TUBING FITTING TYPE",{"$nulls":10},"Compression fitting (Ferrule type) (VTC)"]
[null,11,null,null,"Notes"]
[null,12,null,null,1,"VTC - VENDOR TO CONFIRM "]
[null,13,null,null,2,"Supplier to confirm tubing for specified Pressures and Temperatures"]
[null,14]
[null,15,{"$nulls":13},"VENDOR TO CONFIRM "]
[null,16,null," ","Description",null,null,"End Connection",{"$nulls":4},"Size",null,null,"Quantity",{"$nulls":9},"Connection Material","Notes"]
[null,17,null,null,"SANS 460/2",{"$nulls":7},"15mm",null,null,"12 Of 5.5m lenths (Note 2)"]
[null,18,null,null,"ASME 36.19 SS304 SCH 40",{"$nulls":7},"1/2\""]
[null,19,null,null,"ASME 36.19 SS316 SCH 40",{"$nulls":7},"1\"",null,null,"1 of (Note 2)"]
[null,20,null,null,"ASME 36.19 SS316 SCH 40",{"$nulls":7},"20mm",null,null,"1 of (Note 2)"]
[null,21,null,null,"PID 11 - Main Utilities"]
[null,22,null,null,"End Caps",null,null,"Cu Tube Connection",{"$nulls":4},"15mm",null,null,5,{"$nulls":9},"Brass"]
[null,23,null,null,"Tee Piece",null,null,"3 x Cu Tube Connection",{"$nulls":4},"15mm",null,null,10,{"$nulls":9},"Brass"]
[null,24,null,null,"Elbow",null,null,"2 x Cu Tube Connection",{"$nulls":4},"15mm",null,null,15,{"$nulls":9},"Brass"]
[null,25,null,null,"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"3/4 BSPP male x 15mm Tube",null,null,26,{"$nulls":9},"Brass","15MM x 3/4\" Male connector To Connect 3/4\" Ball Valves and a  To Connect  15mm X 3/4\" Female to Flow Meter"]
[null,27,null,null,"PID 2 - Parr Stirred Digester"]
[null,28,null,null," Female Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 1/2\" BSPF Thread",null,null,1,{"$nulls":9},"Brass","To connnect 6mm Flex Hose nipple connection"]
[null,29,null,null,"Male connector",null,null,"6mm x 1/2\" BSP  Male Pushin Fittings",{"$nulls":4},"6mm x 1/2\" BSP  Male Pushin Fittings",null,null,1,{"$nulls":9},"VTC","15mm copper tube to connect to 6mm polyu tube"]
[null,30,null,null," Female Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 1/2\" BSPF Thread",null,null,1,{"$nulls":9},"VTC","15mm copper tube to connect to 6mm polyu tube"]
[null,31,null,null,"Male connector",null,null,"6mm x 1/2\" BSP  Male Pushin Fittings",{"$nulls":4},"6mm x 1/2\" BSP  Male Pushin Fittings",null,null,1,{"$nulls":9},"VTC","To Connect to polyeurethane 6mm Flex Hose "]
[null,32,null,null,"PID 3 - Flow Through Digester"]
[null,33,null,null,"Male Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 25mm BSP Thread",null,null,1,{"$nulls":9},"Brass","Use thread tape for isolation"]
[null,34,null,null,"EN1092 SS PN40 Blind (#05) Flange",null,null,"DN25 SS316L Flange",{"$nulls":4},"DN25",null,null,1,{"$nulls":9},"SS","Flanged Drilled and tap 1\" BSPF Thread  To suit 15mm copper tube- Thread Tape used as isolation joint between SS Flange and 15mm SANS460/2 tube."]
[null,35,null,null,"Male Connector",null,null,"15MM x 3/4 Male connector",{"$nulls":4},"To Connect for female threaded flange",null,null,1]
[null,36,null,null,"EN1092 SS PN40 Weldneck (#11) Flange",null,null,"DN25 (1inch) SS 316L Flange",{"$nulls":4},"DN25",null,null,1,{"$nulls":10},"To weld onto SS316L Pipe - Bolted to SS Flange on SANS 460/2 tube"]
[null,37,null,null,"Male Connector",null,null,"SS 316L Pipe x SS 316L Threaded End",{"$nulls":4},"1\" SS Tube x 1\" NPT Thread",null,null,1,{"$nulls":9},"VTC","To attach to 1\" Female NPT"]
[null,38,null,null,"PID 6 - Biochar Cooling Tower Make-Up Water"]
[null,39,null,null,"Male Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 15mm BSP Thread",null,null,1,{"$nulls":9},"Brass","To connect 1/2\" Flange"]
[null,40,null,null,"EN1092 SS PN25 Blind (#05) Flange (IMPERIAL)",null,null,"1\" SS304 Flange",{"$nulls":4},"1/2\"",null,null,1,{"$nulls":9},"304 SS","Drill and tap 3/4\" BSP Thread - Thread Tape used as isolation joint between SS Flange and 15mm SANS460/2 tube."]
[null,41,null,null,"EN1092 SS PN25 Weldneck (#11) Flange IMPERIAL",null,null,"1\" SS304 Flange",{"$nulls":4},"1/2\"",null,null,1,{"$nulls":9},"SS306","To be welded to ASME 31.3 SS306 Sch40"]
[null,42,null,null,"Female Connector",null,null,"SS306 SCH40 Pipe Connection x Threaded End",{"$nulls":4},"1/2\" Pipe Connection x 1/2\" BSP Thread ",null,null,1,{"$nulls":9},"SS306"]
[null,43,null,null,"PID 4 - RDH Digester"]
[null,44,null,null,"Tee Piece",null,null,"SS316L Pipe connection x SS316L Pipe connection",{"$nulls":4},"20mm SS Pipe x 20mm SS Pipe",null,null,1,{"$nulls":9},"VTC","To attach to 1\" Female NPT"]
[null,45,null,null,"Elbow",null,null,"SS316L Pipe connection x SS316L Pipe connection",{"$nulls":4},"20mm SS Pipe x 20mm SS Pipe",null,null,6,{"$nulls":9},"VTC"]
[null,46,null,null,"Male Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 20mm BSP Thread",null,null,1,{"$nulls":9},"Brass","Use thread tape for isolation"]
[null,47,null,null,"EN1092 SS PN40 Blind (#05) Flange METRIC",null,null,"DN20 SS316L Flange",{"$nulls":4},"DN20",null,null,1,{"$nulls":9},"SS316","Drill and tap 3/4\" BSP Female Thread - Thread Tape ised as isolation joint between SS Flange and Copper pipe."]
[null,48,null,null,"EN1092 SS PN40 Weldneck (#11) Flange METRIC",null,null,"DN20 SS 316L Flange",{"$nulls":4},"DN20",null,null,3,{"$nulls":9},"SS316","To weld onto SS316L Pipe - Check Bolt positions on RDH Digester Flange before welding. "]
[null,49,null,null,"PID 12 - Steam Boiler"]
[null,50,null,null,"Reducing Female Coupler",null,null,"Brass Threaded End x Cu Tube Connection",{"$nulls":4},"3/4\" BSP Thread x 15mm Cu Tube",null,null,1,{"$nulls":9},"Brass","To attach 3/4\" Male Brass BSP Ball Valve attached to inlet of feed water tank on steam boiler."]

{"sheet":"Hot Water Line","index":3,"n_rows":52,"n_cols":27,"rows_kept":52,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,24],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,24],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,24],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,24],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,24],[12,1,12,2],[12,3,12,5],[12,6,12,9],[12,10,12,13],[12,14,12,17],[12,18,12,24],[13,1,13,2],[13,3,13,5],[13,6,13,9],[13,10,13,13],[13,14,13,17],[13,18,13,24],[14,1,14,2],[14,3,14,5],[14,6,14,9],[14,10,14,13],[14,14,14,17],[14,18,14,24],[15,1,15,24],[16,4,16,11],[16,12,16,24],[17,3,34,3],[17,4,17,11],[17,12,17,14],[17,15,17,24],[18,4,18,11],[18,12,18,14],[18,15,18,24],[19,4,19,11],[19,12,19,14],[19,15,19,24],[20,4,20,8],[20,9,20,11],[20,12,20,14],[20,15,20,24],[21,4,21,11],[21,12,21,14],[21,15,21,18],[21,19,21,20],[21,21,21,22],[22,4,22,11],[22,12,22,14],[22,15,22,24],[23,4,23,11],[23,12,23,14],[23,15,23,24],[24,4,24,11],[24,12,24,14],[24,15,24,24],[25,4,25,11],[25,12,25,14],[25,15,25,24],[26,4,26,11],[26,12,26,14],[26,15,26,24],[27,4,27,11],[27,12,27,14],[27,15,27,24],[28,4,28,11],[28,12,28,14],[28,15,28,24],[29,4,29,24],[30,5,30,24],[31,5,31,24],[32,5,32,24],[33,5,33,24],[34,5,34,24],[35,3,51,3],[35,4,35,6],[35,7,35,11],[35,12,35,14],[35,15,35,24],[35,26,35,29],[36,4,36,6],[36,7,36,11],[36,12,36,14],[36,15,36,24],[37,4,37,6],[37,7,37,11],[37,12,37,14],[37,15,37,24],[38,4,38,29],[39,4,39,6],[39,7,39,11],[39,12,39,14],[39,15,39,24],[40,4,40,6],[40,7,40,11],[40,12,40,14],[40,15,40,24],[41,4,41,6],[41,7,41,11],[41,12,41,14],[41,15,41,24],[42,4,42,6],[42,7,42,11],[42,12,42,14],[42,15,42,24],[43,4,43,6],[43,7,43,11],[43,12,43,14],[43,15,43,24],[44,4,44,6],[44,7,44,11],[44,12,44,14],[44,15,44,24],[45,4,45,6],[45,7,45,11],[45,12,45,14],[45,15,45,24],[45,26,45,29],[46,4,46,6],[46,7,46,11],[46,12,46,14],[46,15,46,24],[46,26,46,29],[47,4,47,28],[48,4,48,6],[48,7,48,11],[48,12,48,14],[48,15,48,24],[48,26,48,29],[49,4,49,29],[50,4,50,6],[50,7,50,11],[50,12,50,14],[50,15,50,24],[50,26,50,29],[51,4,51,6],[51,7,51,11],[51,12,51,14],[51,15,51,24],[51,26,51,29]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-001"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
[null,"Item:",null,null,"Municipal Water Line Connections Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",{"$nulls":4},"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[]
[]
[]
[null,"Data Sheet for Municipal Water Line Line Connections and Tubing"]
[null,"No","Rev","Section","Data",{"$nulls":7},"Description"]
[null,1,null,"DESIGN DATA","TRANSPORTED FLUID",{"$nulls":10},"Potable Water - Municipal Water"]
[null,2,null,null,"LOCATION",{"$nulls":10},"Above Ground"]
[null,3,null,null,"DESIGN LIFE",{"$nulls":10},"25 years"]
[null,4,null,null,"PIPELINE DESIGN PRESSURE",{"$nulls":4},"Barg",{"$nulls":5},15]
[null,5,null,null,"PIPELINE TEMPERATURE - DESIGN ",{"$nulls":5},"°C",null,"MAXIMUM",null,null,40,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,6,null,null,"SERVICE TYPE (Sour/ Non-sour)",{"$nulls":5},"barg",{"$nulls":4},"Non-sour"]
[null,7,null,null,"TUBING MATERIAL",{"$nulls":10},"SANS 460/2 (Metric)"]
[{"$nulls":15},"ASME 31.3 Stainless Steel 306L Piping (Imperial)"]
[null,8,{"$nulls":13},"ASME 31.3 Stainless Steel 316L Piping (Imperial)"]
[null,9,null,null,"TUBING FITTING MATERIAL",{"$nulls":10},"VTC"]
[null,10,null,null,"TUBING FITTING THREAD",{"$nulls":10},"NPT and BSP"]
[null,11,null,null,"TUBING FITTING TYPE",{"$nulls":10},"Compression fitting (Ferrule type) (VTC)"]
[null,12,null,null,"Notes"]
[null,13,null,null,1,"VTC - VENDOR TO CONFIRM "]
[null,14,null,null,2,"Supplier to confirm tubing for specified Pressures and Temperatures"]
[null,15,null,null,3,"TBC - To be confirmed"]
[null,16]
[null,17,{"$nulls":13},"VENDOR TO CONFIRM "]
[null,18,null," ","Description",null,null,"End Connection",{"$nulls":4},"Size",null,null,"Quantity",{"$nulls":9},"Connection Material","Notes"]
[null,19,null,null,"SANS 460/2",null,null,"22mm Copper Tubing",{"$nulls":4},"22mm",null,null,"1 Of 5.5m lenths (Note 2)"]
[{"$nulls":4},"SANS 460/2",null,null,"15mm Copper Tubing",{"$nulls":4},"15mm",null,null,"10 Of 5.5m lenths (Note 2)"]
[null,22,null,null,"PID 11 - Main Utilities"]
[null,23,null,null,"End Caps",null,null,"Cu Tube Connection",{"$nulls":4},"15mm",null,null,2,{"$nulls":9},"Brass"]
[{"$nulls":4},"End Caps",null,null,"Cu Tube Connection",{"$nulls":4},"22mm",null,null,2,{"$nulls":9},"Brass"]
[{"$nulls":4},"Reducing Straight Coupler",null,null,"2 x Cu Tube Connection",{"$nulls":4},"15mm x 22mm",null,null,3,{"$nulls":9},"Brass"]
[null,24,null,null,"Tee Piece",null,null,"3 x Cu Tube Connection",{"$nulls":4},"22mm",null,null,1,{"$nulls":9},"Brass"]
[{"$nulls":4},"Elbow",null,null,"2 x Cu Tube Connection",{"$nulls":4},"22mm",null,null,5,{"$nulls":9},"Brass"]
[null,25,null,null,"Elbow",null,null,"2 x Cu Tube Connection",{"$nulls":4},"15mm",null,null,10,{"$nulls":9},"Brass"]
[{"$nulls":4},"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"3/4\" BSPP x 22mm Tube",null,null,2,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves and a Flow Meter"]
[null,26,null,null,"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"3/4\" BSPP x 15mm Tube",null,null,8,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves and a Flow Meter"]
[null,27,null,null,"PID 8 - Waste Paper Recycler"]
[null,28,null,null,"Female Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 3/4\" BSP Thread",null,null,2,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves and a Flow Meter"]
[null,30,null,null,"PID 9 - Valley Beater"]
[null,31,null,null,"Male Connector",null,null,"Cu Threaded End x Cu Tube Connection",{"$nulls":4},"3/4\" BSPP x 15mm Tube",null,null,2,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves and a Flow Meter"]
[null,32,null,null,"Female Connector",null,null,"Cu Tube Connection x Cu Threaded End",{"$nulls":4},"15mm Tube x 3/4\"BSP Thread",null,null,2,{"$nulls":9},"Brass","To Connect Nickel Plated Brass Ball Valves and a Flow Meter"]

{"sheet":"Steam Line","index":4,"n_rows":49,"n_cols":27,"rows_kept":49,"merged":[[3,1,3,3],[3,4,3,12],[3,13,7,17],[3,18,7,24],[4,1,4,3],[4,4,4,12],[5,1,5,3],[5,4,5,12],[6,1,6,3],[6,4,6,12],[7,1,7,3],[7,4,7,12],[8,1,8,24],[9,1,9,2],[9,3,9,5],[9,6,9,9],[9,10,9,13],[9,14,9,17],[9,18,9,24],[10,1,10,2],[10,3,10,5],[10,6,10,9],[10,10,10,13],[10,14,10,17],[10,18,10,24],[11,1,11,2],[11,3,11,5],[11,6,11,9],[11,10,11,13],[11,14,11,17],[11,18,11,24],[12,1,12,2],[12,3,12,5],[12,6,12,9],[12,10,12,13],[12,14,12,17],[12,18,12,24],[13,1,13,24],[14,4,14,11],[14,12,14,24],[15,3,29,3],[15,4,15,11],[15,12,15,14],[15,15,15,24],[16,4,16,11],[16,12,16,14],[16,15,16,24],[17,4,17,11],[17,12,17,14],[17,15,17,24],[18,4,18,8],[18,9,18,11],[18,12,18,14],[18,15,18,24],[19,4,19,11],[19,12,19,14],[19,15,19,18],[19,19,19,20],[19,21,19,22],[20,4,20,11],[20,12,20,14],[20,15,20,24],[21,4,21,11],[21,12,21,14],[21,15,21,24],[22,4,22,11],[22,12,22,14],[22,15,22,24],[23,4,23,11],[23,12,23,14],[23,15,23,24],[24,4,24,24],[25,5,25,24],[26,5,26,24],[27,5,27,24],[28,5,28,24],[29,5,29,24],[30,3,48,3],[30,4,30,6],[30,7,30,11],[30,12,30,14],[30,15,30,24],[30,26,30,29],[31,4,31,6],[31,7,31,11],[31,12,31,14],[31,15,31,24],[31,26,31,29],[32,4,32,6],[32,7,32,11],[32,12,32,14],[32,15,32,24],[32,26,32,29],[33,4,33,6],[33,7,33,11],[33,12,33,14],[33,15,33,24],[33,26,33,29],[34,4,34,29],[35,4,35,6],[35,7,35,11],[35,12,35,14],[35,15,35,24],[35,26,35,29],[36,4,36,6],[36,7,36,11],[36,12,36,14],[36,15,36,24],[36,26,36,29],[37,4,37,6],[37,7,37,11],[37,12,37,14],[37,15,37,24],[37,26,37,29],[38,4,38,6],[38,7,38,11],[38,12,38,14],[38,15,38,24],[38,26,38,29],[39,4,39,6],[39,7,39,11],[39,12,39,14],[39,15,39,24],[39,26,39,29],[40,4,40,6],[40,7,40,11],[40,12,40,14],[40,15,40,24],[40,26,40,29],[41,4,41,6],[41,7,41,11],[41,12,41,14],[41,15,41,24],[41,26,41,29],[42,4,42,6],[42,7,42,11],[42,12,42,14],[42,15,42,24],[42,26,42,29],[43,4,43,6],[43,7,43,11],[43,12,43,14],[43,15,43,24],[43,26,43,29],[44,4,44,6],[44,7,44,11],[44,12,44,14],[44,15,44,24],[44,26,44,29],[45,4,45,6],[45,7,45,11],[45,12,45,14],[45,15,45,24],[45,26,45,29],[46,4,46,6],[46,7,46,11],[46,12,46,14],[46,15,46,24],[46,26,46,29],[47,4,47,29],[48,4,48,6],[48,7,48,11],[48,12,48,14],[48,15,48,24],[48,26,48,29]]}
[]
[]
[]
[null,"Project",null,null,"BIDF Expansion"]
[null,"Document No:",null,null,"21050-CSI-ME-DAS-001"]
[null,"Location:",null,null,"UKZN CSIR - 359 Mazisi Kunene Rd, Glenwood, Durban"]
[null,"Item:",null,null,"Municipal Water Line Connections Data Sheet"]
[null,"Page:",null,null,"1 of 1"]
[null,"Revision Tracking"]
[null,"Rev No.",null,"Date",null,null,"Prepared",{"$nulls":3},"Checked ",{"$nulls":3},"Approved ",{"$nulls":3},"Status "]
[null,"A",{"$nulls":4},"MJ",{"$nulls":11},"Issued for Internal Review"]
[]
[]
[null,"Data Sheet for Municipal Water Line Line Connections and Tubing and Piping"]
[null,"No","Rev","Section","Data",{"$nulls":7},"Description"]
[null,1,null,"DESIGN DATA","TRANSPORTED FLUID",{"$nulls":10},"STEAM"]
[null,2,null,null,"LOCATION",{"$nulls":10},"Above Ground"]
[null,3,null,null,"DESIGN LIFE",{"$nulls":10},"25 years"]
[null,4,null,null,"PIPELINE DESIGN PRESSURE",{"$nulls":4},"Barg",{"$nulls":5},25]
[null,5,null,null,"PIPELINE TEMPERATURE - DESIGN ",{"$nulls":5},"°C",null,"MAXIMUM",null,null,220,{"$nulls":3},"Note 2",null,"MINIMUM:",null,null,0]
[null,6,null,null,"SERVICE TYPE (Sour/ Non-sour)",{"$nulls":5},"barg",{"$nulls":4},"Non-sour"]
[null,7,null,null,"PIPING MATERIAL",{"$nulls":10},"ASTM A 106 Gr B"]
[null,8,null,null,"FITTING MATERIAL",{"$nulls":10},"VTC"]
[null,9,null,null,"FITTING TYPE",{"$nulls":10},"Socket Weld"]
[null,10,null,null,"Notes"]
[null,11,null,null,1,"VTC - VENDOR TO CONFIRM "]
[null,12,null,null,2,"Supplier to confirm tubing for specified Pressures and Temperatures"]
[null,13,null,null,3,"TBC - To be confirmed"]
[null,14,null,null,4,"SW - Socket Weld"]
[null,15,{"$nulls":13},"VENDOR TO CONFIRM "]
[null,16,null," ","Description",null,null,"End Connection",{"$nulls":4},"Size",null,null,"Quantity",{"$nulls":9},"Connection Material","Notes"]
[null,17,null,null,"ASME 31.3 CS A106 Gr B SCH 40",{"$nulls":7},"1 1/2\" SCH40",null,null,"6 Of 6m lenths (Note 2)",{"$nulls":9},"ASME A106 Gr B","Main Line Piping"]
[null,18,null,null,"ASME 31.3 CS A106 Gr B SCH40",{"$nulls":7},"1/2\" SCH40",null,null,"2 Of 6m lenths (Note 2)",{"$nulls":9},"ASME A106 Gr B","Steam Trap Piping"]
[null,19,null,null,"ASME 31.3 CS A106 Gr B SCH40",{"$nulls":7},"3/8\" SCH40",null,null,"2 Of 6m lenths (Note 2)",{"$nulls":9},"ASME A106 Gr B","RDH Digester Piping Line"]
[null,20,null,null,"PID 12 - Steam Boiler"]
[null,21,null,null,"EN1092 PN25 RF Blind Flange (#5)  IMPERIAL",null,null,"2\" RF BLIND FLANGE",{"$nulls":4},"2\"",null,null,1,{"$nulls":9},"Carbon Steel","Drill 1 1/2\" SCH 40 Hole Thru TO weld to SCH40 Pipe - To bolt to 2\" Boiler EN1092 2500/3 Steam Flange"]
[null,22,null,null,"End Caps",null,null,"A106 Gr B CS SCH40 Pipe Connection SW",{"$nulls":4},"1 1/2\" ",null,null,4,{"$nulls":9},"ASTM A234 "]
[null,23,null,null,"End Caps",null,null,"A106 Gr B CS SCH40 Pipe Connection SW",{"$nulls":4},"3/8\"",null,null,1,{"$nulls":9},"ASTM A234 "]
[null,24,null,null,"Reducing Tee-Piece",null,null,"A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW",{"$nulls":4},"2x1.5\"  Pipe by 1x3/8\"  Pipe",null,null,1,{"$nulls":9},"ASTM A234 "]
[null,25,null,null,"Reducing Tee-Piece",null,null,"A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW",{"$nulls":4},"2x1.5\"  Pipe by 1x1/2\"  Pipe",null,null,2,{"$nulls":9},"ASTM A234"]
[null,26,null,null,"90 degree Angles",null,null,"A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW",{"$nulls":4},"1.5\"  Pipe x 1.5\"  Pipe",null,null,4,{"$nulls":9},"ASTM A234"]
[null,27,null,null,"90 degree Angles",null,null,"A106 Gr B CS SCH40 SW x A106 Gr B CS SCH40 SW",{"$nulls":4},"0.5\" Pipe x 0.5\" Pipe",null,null,12,{"$nulls":9},"ASTM A234"]
[null,28,null,null,"EN1092 PN25 RF Slip On Flange (#1) IMPERIAL",null,null,"1.5\" RF SLIP ON FLANGE",{"$nulls":4},"1.5\"",null,null,2,{"$nulls":9},"ASTM A234","For steam trap low point drain ball valve"]
[null,29,null,null,"EN1092 NP25 RF Blind Flange (#5) IMPERIAL",null,null,"1.5\" RF BLIND FLANGE",{"$nulls":4},"1.5\"",null,null,2,{"$nulls":9},"ASTM A234","Drill 1/2\" SCH 40 Hole Thru TO weld to SCH40 Pipe - To bolt to 1.5\" EN 1092-1 STEAM TRAP DRAIN BALL VALVE PIPE"]
[null,30,null,null,"Tee-Piece",null,null,"A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW",{"$nulls":4},"1.5\"",null,null,5,{"$nulls":9},"ASTM A234","STEAM TRAP AND AIR VENT BRANCH, PLUS MAINLINE BRANCHES"]
[null,31,null,null,"Tee-Piece",null,null,"A106 Gr B CS SCH40 SWx A106 Gr B CS SCH40 SW",{"$nulls":4},"0.5\"",null,null,6,{"$nulls":9},"ASTM A234"]
[null,32,{"$nulls":23},"ASTM A234"]
[null,33,null,null,"PID 4 - RDH DIGESTER"]
[null,34,null,null,"EN1092 PN40 RF Slip On Flange (#1) METRIC",null,null,"DN20 RF SLIP ON FLANGE",{"$nulls":4},"DN 20",null,null,1,{"$nulls":9},"ASTM A234","To connect steam line to RDH digester"]